{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":29,"n_cols":10,"rows_kept":29,"cut":false,"hidden":false,"merged":[[26,1,26,2],[27,1,27,2],[28,1,28,2],[25,1,25,2],[1,1,1,3],[1,5,1,9],[17,5,17,9],[17,1,17,2],[19,1,19,2],[18,1,18,2],[28,4,28,9],[2,1,3,2],[4,1,6,2],[7,1,9,2],[11,1,11,2],[12,1,12,2],[10,1,10,2],[13,1,13,2],[13,4,13,9],[14,1,14,2],[15,4,15,9],[15,1,15,2],[16,1,16,2],[20,1,20,2],[20,4,20,9],[21,1,24,1],[21,4,21,9],[22,4,22,9],[23,4,23,9],[26,4,26,9],[27,4,27,9]]}
[]
[null,"Indoor Unit",null,null,null,"Compact 4-Way Cassette Type"]
[null,"Model\nPower Supply",null,"AC1Ф, 220-240V/50Hz","AVC-05URCSAB","AVC-07URCSAB","AVC-09URCSAB","AVC-12URCSAB","AVC-14URCSAB","AVC-17URCSAB"]
[null,null,null,"AC1Ф, 220/60Hz","——","AVC-07UR2SAB","AVC-09UR2SAB","AVC-12UR2SAB","AVC-14UR2SAB","AVC-17UR2SAB"]
[null,"Nominal Cooling Capacity",null,"kW",1.7,2.2000000000000002,2.8,3.6,4.3,5]
[null,null,null,"kcal/h",1500,1900,2400,3100,3700,4300]
[null,null,null,"Btu/h",5800,7500,9600,12300,14700,17100]
[null,"Nominal Heating Capacity",null,"kW",1.9,2.8,3.3,4.2,4.9000000000000004,5.6]
[null,null,null,"kcal/h",1700,2400,2800,3600,4200,4800]
[null,null,null,"Btu/h",6500,9600,11300,14300,16700,19100]
[null,"Power Input",null,"W"]
[null,"Sound Pressure Level(High/Medium/Low)",null,"dB(A)","39-34-30","39-34-30","39-34-30","39-34-30","41-38-33","44-41-37"]
[null,"Indoor Fan Air Flow Rate (High/Medium/Low)",null,"m3/h","570/480/384","570/480/384","570/480/384","570/480/384","654/564/456","792/690/588"]
[null,"Outer Dimensions   (H×W×D)",null," mm","270×570×570"]
[null,"Net Weight",null,"kg",20,20,20,20,20,20]
[null,"Refrigerant",null,null,"R410A(Nitrogen-charged for Corrosion-resistance)"]
[null,"Motor Power",null,"W",63,63,63,63,71,89]
[null,"Connections Refrigerant Piping",null,null,null,"Flare-nut Connection(with Flare Nuts)"]
[null,"Liquid Line",null,"mm","Ф6.35","Ф6.35","Ф6.35","Ф6.35","Ф6.35","Ф6.35"]
[null,"Gas Line",null,"mm","Ф12.7","Ф12.7","Ф12.7","Ф12.7","Ф12.7","Ф12.7"]
[null,"Condensate Drain  (Outer Diameter)",null,"mm","Ф32"]
[null,"Panel","Model",null,"HPE-CR-NA"]
[null,null,"Cabinet Color ",null,"Neutral White"]
[null,null,"Outer Dimensions (H×W×D)",null,"30×650×650"]
[null,null,"Net Weight",null,2.4,2.4,2.4,2.4,2.4,2.4]
[null,"Packing Volume",null,"m³",7.0000000000000007E-2,7.0000000000000007E-2,7.0000000000000007E-2,7.0000000000000007E-2,7.0000000000000007E-2,7.0000000000000007E-2]
[null,"Wireless Remote Controller/Receiver",null,null,"Standard Equiped Wireless Remote Control HYE-Q01+Receiver"]
[null,"Wired Remote Controller",null,null,"Optional"]
[null,"Drain pump",null,null,"Standard"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}