{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":26,"n_cols":12,"rows_kept":26,"cut":false,"hidden":false,"merged":[[19,1,19,2],[20,1,20,2],[25,1,25,2],[12,1,12,2],[13,4,13,7],[14,4,14,7],[25,4,25,11],[22,1,22,2],[16,4,16,11],[21,1,21,2],[21,4,21,11],[23,1,23,2],[24,1,24,2],[23,4,23,11],[24,4,24,11],[16,1,16,2],[17,1,17,2],[18,1,18,3],[18,5,18,11],[10,1,11,1],[0,1,0,3],[0,5,0,11],[3,1,5,2],[6,1,8,2],[1,1,2,2],[9,1,9,2],[15,1,15,2],[13,1,13,2],[13,8,13,10],[14,1,14,2],[14,8,14,10]]}
[null,"Indoor Unit",null,null,null,"Floor&Ceiling"]
[null,"Model \nPower Supply",null,"220-240V/50HZ","AVV-17URSCA","AVV-18URSCA","AVV-22URSCA","AVV-24URSCA","AVV-27URSCB","AVV-30URSCB","AVV-38URSCB","AVV-48URSCC"]
[null,null,null,"AC1Ф, 220/60Hz","AVV-17UR2SA","AVV-18UR2SA","AVV-22UR2CA","AVV-24UR2SA","AVV-27UR2SB","AVV-30UR2SB","AVV-38UR2SB","AVV-48UR2SC"]
[null,"Nominal Cooling Capacity",null,"Kw",5,5.6,6.3,7.1,8.4,9,11.2,14.2]
[null,null,null,"kcal/h",4300,4800,5400,6100,7200,7700,9600,12200]
[null,null,null,"Btu/h",17100,19100,21500,24200,28700,30700,38200,48500]
[null,"Nominal Heating Capacity",null,"Kw",5.6,6.5,7.5,8.5,9.6,10,13,16.3]
[null,null,null,"kcal/h",4800,5600,6500,7300,8300,8600,11200,14000]
[null,null,null,"Btu/h",19100,22200,25600,29000,32800,34100,44400,55600]
[null,"Power Input",null,"W",40,40,70,70,70,80,130,160]
[null,"Sound Pressure Level","Ceiling","dB(A)","39/35/30","39/35/30","45/41/37","45/41/37","43/39/34","45/40/36","51/46/40","50/46/42"]
[null,null,"Floor","dB(A)","43/38/35","43/38/35","48/44/40","48/44/40","46/41/37","48/43/39","54/49/43","55/50/46"]
[null,"Indoor Fan Air Flow Rate(High\\Medium\\Low)",null,"m³/h","780/660/540","780/660/540","966/840/678","966/840/678","1092/912/732","1164/978/798","1488/1230/978","1980/1680/1380"]
[null,"Outer Dimensions",null,"mm","990x680x230",null,null,null,"1285x680x230",null,null,"1580x680x230"]
[null,"Packing Dimensions",null,"mm","1110x830x340",null,null,null,"1400x830x340",null,null,"1690x830x340"]
[null,"Net Weight",null,"kg",31,31,32,32,39,40,41,47]
[null,"Refrigerant",null,null,"R410A(Nitrogen-charged for Corrosion-resistance)"]
[null,"Motor Power",null,"W",40,40,70,70,70,80,130,160]
[null,"Connection Refrigerant Piping",null,null,null,"Flare-nut Connection(with Flare Nuts)"]
[null,"Liquid Line",null,"mm","Φ6.35","Φ6.35","Φ9.53","Φ9.53","Φ9.53","Φ9.53","Φ9.53","Φ9.53"]
[null,"Gas Line",null,"mm","Φ15.88","Φ15.88","Φ15.88","Φ15.88","Φ15.88","Φ15.88","Φ15.88","Φ15.88"]
[null,"Condensate Drain  (Outer Diameter)",null,"mm","Ф32"]
[null,"Packing Volume",null,"m³",0.31,0.31,0.31,0.31,0.4,0.4,0.4,0.48]
[null,"Wireless Remote Controller/Receiver",null,null,"Standard Equiped with HYE-Q01+Receiver"]
[null,"Wired Remote Controller",null,null,"Optional"]
[null,"Drain pump",null,null,"NO"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}