{"text_format":"2","workbook":"xlsx","n_sheets":2,"sheets":["技术参数表","Sheet2"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"技术参数表","index":0,"n_rows":32,"n_cols":24,"rows_kept":32,"cut":false,"hidden":false,"merged":[[15,21,15,23],[15,5,15,7],[15,9,15,10],[15,11,15,15],[15,16,15,17],[15,18,15,20],[30,3,30,23],[31,0,31,14],[14,9,14,10],[21,0,23,0],[24,0,24,1],[29,0,30,0],[28,0,28,1],[25,0,25,1],[26,0,27,0],[18,0,18,1],[19,0,19,1],[15,3,15,4],[14,11,14,15],[29,3,29,23],[14,18,14,20],[14,21,14,23],[5,1,6,1],[9,0,12,0],[0,1,0,2],[2,0,4,2],[1,1,1,2],[9,1,10,1],[2,3,4,3],[2,4,4,4],[20,0,20,1],[20,3,20,23],[13,0,13,1],[14,0,14,1],[15,0,15,1],[16,0,16,1],[17,0,17,1],[14,16,14,17],[2,5,4,5],[2,6,4,6],[2,7,4,7],[14,3,14,4],[14,5,14,7],[5,0,8,0]]}
["R Hi-efficiency Series","HP",null,"8HP","10HP","12HP","14HP","16HP","18HP","20HP","22HP","24HP","26HP","28HP","30HP","32HP","34HP","36HP","38HP","40HP","42HP","44HP","46HP","48HP"]
["Model Power Supply","AC3 380V～415V/50Hz",null,"AVWT-76FESRA","AVWT-96FESRA","AVWT-114FESSA","AVWT-136FESSA","AVWT-154FESSA","AVWT-170FESZA","AVWT-190FESZA","AVWT-212FESZA","AVWT-232FESZA","AVWT-250FESZA","AVWT-272FESZA","AVWT-290FESZA","AVWT-308FESZA","AVWT-324FESZA","AVWT-340FESZA","AVWT-364FESZA","AVWT-382FESZA","AVWT-398FESZA","AVWT-420FESZA","AVWT-438FESZA","AVWT-454FESZA"]
["Combination",{"$nulls":7},"AVWT-76*","AVWT-76*","AVWT-76*","AVWT-114*","AVWT-114*","AVWT-136*","AVWT-136*","AVWT-154*","AVWT-96*","AVWT-96*","AVWT-96*","AVWT-96*","AVWT-96*","AVWT-114*","AVWT-136*","AVWT-154*"]
[{"$nulls":8},"AVWT-96*","AVWT-114*","AVWT-136*","AVWT-114*","AVWT-136*","AVWT-136*","AVWT-154*","AVWT-154*","AVWT-96*","AVWT-96*","AVWT-114*","AVWT-136*","AVWT-154*","AVWT-154*","AVWT-154*","AVWT-154*"]
[{"$nulls":16},"AVWT-136*","AVWT-154*","AVWT-154*","AVWT-154*","AVWT-154*","AVWT-154*","AVWT-154*","AVWT-154*"]
["Cooling Operation","Norminal Capacity","KW",22.4,28,33.5,40,45,50,56,61.5,69,73,80,85,90,95,100,109,112,118,125,132,136]
[null,null,"KBtu/h",76.4505056,95.563131999999996,114.3344615,136.51875999999999,153.5,170.64845,190.8,213,232,250.8,273,290,307,324.10000000000002,341.2,365.1,382.1,399.2,421.4,438.4,455.5]
[null,"Power Consumption ","KW",5.32,6.97,9.18,10.81,13.16,{"$f":"D8+E8","v":12.29},{"$f":"D8+F8","v":14.5},{"$f":"D8+G8","v":16.130000000000003},{"$f":"F8+F8","v":18.36},{"$f":"F8+G8","v":19.990000000000002},{"$f":"G8+G8","v":21.62},{"$f":"G8+H8","v":23.97},{"$f":"H8+H8","v":26.32},{"$f":"E8+E8+G8","v":24.75},{"$f":"E8+E8+H8","v":27.1},{"$f":"E8+F8+H8","v":29.31},{"$f":"E8+G8+H8","v":30.94},{"$f":"E8+H8+H8","v":33.29},{"$f":"F8+H8+H8","v":35.5},{"$f":"G8+H8+H8","v":37.129999999999995},{"$f":"H8+H8+H8","v":39.480000000000004}]
[null,"EER",null,{"$f":"D6/D8","v":4.2105263157894735},{"$f":"E6/E8","v":4.0172166427546632},3.6492374727668846,3.700277520814061,3.4194528875379939,4.0683482506102528,3.8620689655172415,3.812771233725976,3.7581699346405228,3.6518259129564781,3.700277520814061,3.5460992907801421,3.4194528875379939,3.8383838383838382,3.6900369003690034,3.7188672807915388,3.6199095022624435,3.5446079903875036,3.5211267605633805,3.5550767573390791,3.444782168186423]
["Heating Operation","Norminal Capacity","KW",25,31.5,37.5,45,50,56,63,69,77.5,82.5,90,95,100,106,{"$f":"I10+I10","v":112},118,125,{"$f":"J10+K10","v":132},140,145,150]
[null,null,"KBtu/h",85.3,107.5,128,153.5,170.6,191.1,213.3,239,261,281.5,307.10000000000002,324.10000000000002,341.2,361.7,382.1,409.5,426.5,447.5,472.6,494.7,511.8]
[null,"Power Consumption ","KW",5.4,7.19,8.6,10.199999999999999,12.5,{"$f":"D12+E12","v":12.59},{"$f":"D12+F12","v":14},{"$f":"D12+G12","v":15.6},{"$f":"F12+F12","v":17.2},{"$f":"F12+G12","v":18.799999999999997},{"$f":"G12+G12","v":20.399999999999999},{"$f":"G12+H12","v":22.7},{"$f":"H12+H12","v":25},{"$f":"E12+E12+G12","v":24.58},{"$f":"E12+E12+H12","v":26.880000000000003},{"$f":"E12+F12+H12","v":28.29},{"$f":"E12+G12+H12","v":29.89},{"$f":"E12+H12+H12","v":32.19},{"$f":"F12+H12+H12","v":33.6},{"$f":"G12+H12+H12","v":35.200000000000003},{"$f":"H12+H12+H12","v":37.5}]
[null,"COP",null,{"$f":"D10/D12","v":4.6296296296296298},{"$f":"E10/E12","v":4.3810848400556326},4.3604651162790695,4.4117647058823533,4,4.4479745830023827,4.5,4.4230769230769234,4.5058139534883725,4.3882978723404262,4.4117647058823533,4.1850220264317182,4,4.3124491456468679,4.1666666666666661,4.1710851891127607,4.1820006691201073,4.1006523765144456,4.1666666666666661,4.1193181818181817,4]
["Air Flow Rate",null,"m3/min",170,175,195,195,195,{"$f":"D14+E14","v":345},{"$f":"D14+F14","v":365},{"$f":"D14+G14","v":365},{"$f":"F14+F14","v":390},{"$f":"F14+G14","v":390},{"$f":"G14+G14","v":390},{"$f":"G14+H14","v":390},{"$f":"H14+H14","v":390},{"$f":"E14+E14+G14","v":545},{"$f":"E14+E14+H14","v":545},{"$f":"E14+F14+H14","v":565},{"$f":"E14+G14+H14","v":565},{"$f":"E14+H14+H14","v":565},{"$f":"F14+H14+H14","v":585},{"$f":"G14+H14+H14","v":585},{"$f":"H14+H14+H14","v":585}]
["Out Dimension",null,"mm","1720×950×750",null,"1720×1210×750",null,null,"1720×(950+950)×750","1720×(950+1210)×750",null,"1720×(1210+1210)×750",{"$nulls":4},"1720×(950+950+1210)×750",null,"1720×(950+1210+1210)×750",null,null,"1720×(1210+1210+1210)×750"]
["Packing Dimension",null,"mm","1828×1018×824",null,"1828×1278×824",null,null,"1828×(1018+1018)×824","1828×(1018+1278)×824",null,"1828×(1278+1278)×824",{"$nulls":4},"1828×(1018+1018+1278)×824",null,"1828×(1018+1278+1278)×824",null,null,"1828×(1278+1278+1278)×824"]
["Net Weight",null,"kg",245,246,311,312,318,{"$f":"D17+E17","v":491},{"$f":"D17+F17","v":556},{"$f":"D17+G17","v":557},{"$f":"F17+F17","v":622},{"$f":"F17+G17","v":623},{"$f":"G17+G17","v":624},{"$f":"G17+H17","v":630},{"$f":"H17+H17","v":636},{"$f":"E17+E17+G17","v":804},{"$f":"E17+E17+H17","v":810},{"$f":"E17+F17+H17","v":875},{"$f":"E17+G17+H17","v":876},{"$f":"E17+H17+H17","v":882},{"$f":"F17+H17+H17","v":947},{"$f":"G17+H17+H17","v":948},{"$f":"H17+H17+H17","v":954}]
["Gross Weight",null,"kg",255,255,325,325,330,{"$f":"D18+E18","v":510},{"$f":"D18+F18","v":580},{"$f":"D18+G18","v":580},{"$f":"F18+F18","v":650},{"$f":"F18+G18","v":650},{"$f":"G18+G18","v":650},{"$f":"G18+H18","v":655},{"$f":"H18+H18","v":660},{"$f":"E18+E18+G18","v":835},{"$f":"E18+E18+H18","v":840},{"$f":"E18+F18+H18","v":910},{"$f":"E18+G18+H18","v":910},{"$f":"E18+H18+H18","v":915},{"$f":"F18+H18+H18","v":985},{"$f":"G18+H18+H18","v":985},{"$f":"H18+H18+H18","v":990}]
["Compressor Quantity",null,null,1,1,2,2,2,{"$f":"D19+E19","v":2},{"$f":"D19+F19","v":3},{"$f":"D19+G19","v":3},{"$f":"F19+F19","v":4},{"$f":"F19+G19","v":4},{"$f":"G19+G19","v":4},{"$f":"G19+H19","v":4},{"$f":"H19+H19","v":4},{"$f":"E19+E19+G19","v":4},{"$f":"E19+E19+H19","v":4},{"$f":"E19+F19+H19","v":5},{"$f":"E19+G19+H19","v":5},{"$f":"E19+H19+H19","v":5},{"$f":"F19+H19+H19","v":6},{"$f":"G19+H19+H19","v":6},{"$f":"H19+H19+H19","v":6}]
["Condenser Fan Quantity",null,null,1,1,1,1,1,2,2,2,2,2,2,2,2,3,3,3,3,3,3,3,3]
["Cabinet Color",null,null,"Lvory White"]
["Refrigerant Piping","Low Gas Line","mm","φ19.05","φ22.2","φ25.4","φ25.4","φ28.6","φ28.6","φ28.6","φ28.6","φ28.6","φ31.75","φ31.75","φ31.75","φ31.75","φ31.75","φ31.75","φ38.1","φ38.1","φ38.1","φ38.1","φ38.1","φ38.1"]
[null,"High Gas Line","mm","φ15.85","φ19.05","φ22.2","φ22.2","φ22.2","φ22.2","φ22.2","φ25.4","φ25.4","φ25.4","φ28.6","φ28.6","φ28.6","φ28.6","φ28.6","φ31.75","φ31.75","φ31.75","φ31.75","φ31.75","φ31.75"]
[null,"Liquid Line","mm","φ9.53","φ9.53","φ12.7","φ12.7","φ12.7","φ15.88","φ15.88","φ15.88","φ15.88","φ19.05","φ19.05","φ19.05","φ19.05","φ19.05","φ19.05","φ19.05","φ19.05","φ19.05","φ19.05","φ19.05","φ19.05"]
["Max.number of connectable IDU",null,null,13,16,19,23,26,26,33,36,40,43,47,50,53,56,59,64,64,64,64,64,64]
["Max.Piping Length",null,"m",1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000,1000]
["Height Difference","Between ODU&IDU","m","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)","50/40(90/70*)"]
[null,"Between IDUS","m",15,15,15,15,15,15,15,15,15,15,15,15,15,15,15,15,15,15,15,15,15]
["Noise level",null,"dB(A)",60,60,62,62,63,62,63,63,64,64,64,65,65,66,66,67,67,67,67,67,68]
["Operation Range","Cooling","℃ DB","-5℃～48℃"]
[null,"Heating","℃ WB","-20℃～15.5℃ "]
["Note: For connection with \" * \" please contact with our technical engineer."]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}